## IMS-0105.027I Weekly Inspection
UPU Industries, Inc. | Unnamed: 1 | Sprinkler System Weekly Inspection Checklist IMS-0105.027I | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Revision: 2 | Unnamed: 8
Prepared by: I Graf | [6 empty] | Revision date: 20 Jun 2019
Updated by: L Heath | [6 empty] | Effective date: 18 Sep 2013
Approved: K Rogers | [6 empty] | Page 1 of 1
This form covers a 6-month period |  |  |  |  | January - June
| Year: | 2024 | System: | WET
1. If valves are sealed, note "Yes" in this block. If any are not sealed, reseal and note "Resealed" in this block.
2. If all sprinklers are in good condition and storage is maintained at least 18 in. (46 cm) below the sprinklers, note "Yes" in block. If not, write "See Notes" and briefly describe under the "Notes/Repair WO#" section.
3. If there is the proper number and type of replacement sprinkler heads and a sprinkler wrench accounted for, put "Yes", if not, write "See Notes" and briefly describe under the "Notes/Repair WO#" section.
4. Record pressure readings in psi (bar). A loss of more than 10% should be investigated.
5. If no damage is found to the sprinkler system, note "Yes" in this block. If there is physical damage mark "Damaged" and briefly describe under the "Notes/Repair WO#" section.
6. If all ID Signs are attached, note "Yes" in block. If not, write "See Notes" and briefly describe under the "Notes/Repair WO#" section.
Date | Inspector | Valves Sealed (1) | Sprinkler Heads OK (2) | All Alarm Devices Seen (3) | Note Water Pressures (4) | Free of Damage (5) | ID Signs Attached (6) | Notes/ Repair WO#
2024-01-05 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-01-12 | JS | yes | yes | yes | 110110110 | yes | yes | main 100 psi
2024-01-19 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-01-26 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-02-01 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-02-07 | JS | yes | yes | yes | 110110110 | yes | yes | main 100 psi
2024-02-14 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-02-21 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-02-28 | JS | yes | yes | yes | 110110115 | yes | yes | main 100 psi
2024-03-06 | AP | yes | yes | yes | 110110110 | yes | yes | main 100 psi
2024-03-13 | AP | yes | yes | yes | 110110115 | yes | yes | main 100 psi
2024-03-20 | JS | yes | yes | yes | 115115115 | yes | yes | main 100 psi
2024-03-25 | AP | yes | yes | yes | 115115115 | yes | yes | main 110 psi
2024-04-02 | AP | yes | yes | yes | 115115115 | yes | yes | main 115 psi
2024-04-12 | AP | yes | yes | yes | 150150150 | yes | yes | main 115 psi
2024-04-16 | RM | yes | yes | yes | 150, 150, 150 | yes | yes | main 115 psi
2024-04-23 | RM | yes | yes | yes | 150, 150, 150 | yes | yes | main 115 psi
2024-05-02 | RM | yes | yes | yes | 145, 145, 145 | yes | yes | main 120 psi
2024-05-08 | RM | YES | YES | YES | 145, 145, 145 | YES | YES | main 115-120 psi
2023-05-16 | RM | YES | YES | YES | 150, 150, 150 | YES | YES | main 115-120 psi
2024-05-21 | RM | YES | YES | YES | 150, 150, 150 | YES | YES | main 115 psi
2024-05-31 | RM | YES | YES | YES | 145, 145, 145 | YES | YES | main 115 psi
2024-06-06 | RM | YES | YES | YES | 145, 145, 145 | YES | YES | main 118 psi
2024-06-13 | RM | YES | YES | YES | 120, 120, 120 | YES | YES | main 115 psi
2024-06-27 | RM | YES | YES | YES | 145, 145, 145 | YES | YES | main 125 psi
2024-07-12 | TC | YES | YES | YES | 145145145 | YES | YES | main 118 psi
22-JUL-24 | TC | YES | YES | YES | 140,140,140 YES YES |  |  | main 122psi
1-AUG-24 | TC | YES | YES | YES | 140140140 | YES | YES | main 118psi
9-AUG-24 | TC | YES | YES | YES | 137137136 | YES | YES | main 118psi
15-AUG-24 | TC | YES | YES | YES | 140-140-140 | YES | YES | main 119psi
23-AUG-24 | TC | YES | YES | YES | 132-132-130 | YES | YES | main 120psi
29 AUG 24 | TC | YES | YES | YES | 126-126-126 | YES | YES | main 120psi
5 SEPT 24 | TC | YES | YES | YES | 130-130-130 YES |  | YES | main 120psi
13 SEPT 24 | TC YES YES YES 125-125-125 YES YES main 120psi
18 SEPT 24 | TC | YES | YES | YES | 120-125-120 | YES | YES | main 120psi
2024-09-24 | RC | YES | YES | YES | 120-120-120 | YES | YES | main 120 psi
9 OCT 24 | TC | YES | YES | YES | 125-125-125 | YES | YES | main 120 psi
16 OCT 24 | TC | YES | YES | YES | 132-133-131 | YES | YES | main 120 psi
2024-10-17 | TC | YES | YES | YES | 130-131-130 | YES | YES | main 120 psi
29 OCT 24 | TC | YES | YES | YES | 142-144-141 | YES | YES | main 120 psi